## Forward
THERMAL RATING
PRODUCT MODEL: ID-THERMAL/TOWER
VERSION: 6.01
FINAL ISSUE DATE: May 22, 2001
WARNING!!!
PLEASE DO NOT DELETE OR ADD THE COLUMNS OR ROWS TO THE SHEETS !!!!!
THE PROCEDURE FOR THE AUTOMATIC WORKS MAKES AN ERROR MESSAGE IF YOU DELETE
OR ADD THE COLUMNS OR ROWS.
YOU CAN ONLY CHANGE THE INPUT DATA COLORED WITH BLUE AND CAN RUN THE PROGRAMS
WITH THE PUSH OF BUTTON.
THIS PROGRAM IS RUN ON MICROSOFT EXCEL 97 OR LATER VERSION.
IF YOU HAVE ANY QUESTIONS, PLEASE CALL OR WRITE TO ME IN SEOUL, KOREA.
HOMEPAGE: http://myhome.hananet.net/~criok
E-MAIL: criok@hanmir.com
TEL: (02)786-4237, FAX: (02)786-4247
DAEIL AQUA CO., LTD.
Click Here!!!

## Input
INPUT (Tower Design Conditions)
Site Altitude | 0 | ft | % Obstruction @Fill | 1.5%
Wet Bulb Temperature | 80.6 | oF | % By-Pass Wall Water | 2%
Relative Humidity | 80% |  | PD Coefficient @Drift Eliminator | 2
Number of Cells | 3 |  | Fan Total Efficiency | 79.3%
Design Water Flow Rate | 26417 | gpm | Power Transmission Efficiency | 91.3%
Cell Length | 28.22 | ft | Motor Power Margin | 13.5%
Cell Width | 36.09 | ft | Motor Power | 125 | hp
Type of Air Inlet | Two Sides Open |  | Fan Diameter | 22 | ft
Air Inlet height | 13.12 | ft | Number of Fan per Cell | 1
% Obstruction @Air Inlet | 10% |  | Seal Disk Diameter | 76 | inch
PD Coefficient @Air Inlet | 1.5 |  | PD Coefficient @Fan Inlet | 0.15
Fill Model | CF 1900 |  | Venturi Height of Stack | 6.56 | ft
Fill Depth | 4.9213 | ft | Design Hot Water Temperature | 104 | oF
PD Fill Multiplying Factor | 1.05 |  | Design Cold Water Temperature | 89.6 | oF
Fill KaV/L Multiplying Factor | 0.95 |  | KaV/L Correction Factor | 0.3164
RESULT (Basic Thermal Rating)
Water Through Tower | 25888.6602 | gpm | Air Volume per Fan | 642316.1525 | acfm
Computed L/G Ratio | 1.6814 |  | Net Fan Area per Fan | 348.6303 | ft2
Air Mass Flow Rate | 128307.7073 | Lb/min | Air Velocity @Fan | 1842.3989 | fpm
Tower Exit Air Temperature | 98.4617 | oF | Velocity Pressure @Fan | 0.19524 | inch Aq.
Air Density @Tower Exit | 0.06932 | Lb/ft3 | Net Fan Power | 98.7181 | bhp
Air Specific Volume @ Tower Exit | 15.0182 | ft3/Lb | Total Fan Static Pressure | 0.57941 | inch Aq.
RESULT (NTU)
WATER SIDE | tw (oF) | hw (BTU/lb') | AIR SIDE | ha (BTU/lb') | 1/(hw -ha)
Cold Water Temp through Tower | 88.7976 |  | Inlet Air Enthalpy | 44.344
tw1 + 0.1 x Act_Range | 90.267 | 56.3218 | ha1 + 0.1 x Delta ha | 46.8147 | 0.10518
tw1 + 0.4 x Act_Range | 94.6752 | 62.8329 | ha1 + 0.4 x Delta ha | 54.2267 | 0.11619
tw1 + 0.6 x Act_Range | 97.614 | 67.6046 | ha1 + 0.6 x Delta ha | 59.168 | 0.11853
tw1 + 0.9 x Act_Range | 102.0221 | 75.4898 | ha1 + 0.9 x Delta ha | 66.5799 | 0.11224
|  |  | Tower Demand (NTU) |  | 1.6609
RESULT (Pressure Drops Calculation)
1) Air Inlet |  |  | 3) Drift Eliminator
- Total Net Air Inlet | 1999.3304 | ft2 | - Net Area | 3009.5486 | ft2
- Air Density | 0.071691 | Lb/ft3 | - Air Density | 0.06932 | Lb/ft3
- Specific Volume | 14.2495 | ft3/Lb | - Specific Volume | 15.0182 | ft3/Lb
- Total Air Volume | 9198.5163 | acfm | - Air Volume | 1926948.4625 | acfm
- Air Velocity | 914.4695 | fpm | - Air Velocity | 640.2782 | fpm
- Pressure Drop | 0.074615 | INCH Aq. | - Pressure Drop | 0.047158 | inch Aq.
2) Fill |  |  | 4) Fan Inlet
- Total Net Fill Area | 3009.5486 | ft2 | - Air Density | 0.06932 | Lb/ft3
- Water Loading | 8.6022 | gpm/ft2 | - Air Velocity @Fan | 1842.3989 | fpm
- Average Air Density | 0.070506 | Lb/ft3 | - Pressure Drop | 0.029285 | inch Aq.
- Average Air Specific Volume | 14.6238 | ft3/Lb | 5. Velocity Recovery
- Average Air Volume per Cell | 1876342.5306 | acfm | - Efficiency of Fan Stack | 74.04%
- Average Fill Air Velocity | 623.4631 | fpm | - Air Density | 0.06932 | Lb/ft3
- Pressure Drop | 0.46395 | inch Aq. | - Velocity Recovery | 0.035592 | inch Aq.
Final Cold Water Temperature
Approach | 8.4915 | oF | Final Cold Water Temp. | 89.0915 | oF
RUN PROGRAM

## Calculation
Inlet Dry Bulb Temperature Estimation
Altitude | Feet | 0
Inlet Wet Bulb Temperature | oF | 80.6
Inlet Air Enthalpy @ WBT | BTU/LB' | #VALUE!
Relative Humidity | % | 80%
Inlet Air Enthalpy @ DBT & RH | BTU/LB' | #VALUE!
Inlet Dry Bulb Temperature | oF | 85.8779
Inlet Air Density | Lb/FT3 | #VALUE!
Inlet Air Specific Volume | FT3/LB' | #VALUE!
Exit Air Wet Bulb Temperature Estimation
L/G Ratio |  | 1.6814
Cooling Range Through Tower | oF | 14.6939
Exit Air Enthalpy Based On Estimation | BTU/LB' | #VALUE!
Equivalent Exit Air Enthalpy | BTU/LB' | #VALUE!
Equivalent Exit Wet Bulb Temperature | oF | 98.4617
Exit Air Density | LB/FT3 | #VALUE!
Exit Specific Volume | FT3/LB' | #VALUE!
Fan Air Volume Estimation
Fan Net Power @ Design | HP | 98.7181
Total Pressure Drop | Inch Aq. | 0.57941
Velocity Pressure @ Fan | Inch Aq. | 0.19524
Fan Efficiency |  | 79.3%
Fan Net Power | HP | 98.7182
Predicted Air Volume | ACFM | 642316.1525
Approach Estimation
Tower Characteristic |  | 1.9669
Water Side | Air Side | 1/(hw-ha)
88.7976 | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
NTU |  | #VALUE!
NEW APPROACH |  | 8.4915
1.661